## Sheet1
| Controller Information |  |  | Points
| Description | Location |  | Name/Label | Value | Units/States | Description | Location
| HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC004 | HWS.DHWS-T | 116.3815 | deg F | Domestic HW Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.DHWS-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.DHWS-T
x |  |  |  | HWS.PHWS-T | 140.6453 | deg F | Primary HW Supply Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWS-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWS-T
x |  |  |  | HWS.PHWR-T | 132.2234 | deg F | Primary HW Return Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWR-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWR-T
x |  |  |  | HWS.HX1V2-O | 0.54986 | % | Heat Exchanger 1 Valve 2 Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HX1V2-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HX1V2-O
x |  |  |  | HWS.HX1V1-O | 58.6363 | % | Heat Exchanger 1 Valve 1 Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HX1V1-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HX1V1-O
x |  |  |  | HWS.MAD-O | 99.9982 | % | Mixed Air Damper Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MAD-O
|  |  |  | HWS.RADOATLOCKOUT-SP | 60 | deg F | Radiant Heating Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RADOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RADOATLOCKOUT-SP
|  |  |  | HWS.HWMAX-SP | 190 | deg F | Maximum HW Temp Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWMAX-SP
|  |  |  | HWS.HWMIN-SP | 140 | deg F | Minimum HW Temp Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWMIN-SP
|  |  |  | HWS.HTGOATLOCKOUT-SP | 65 | deg F | Heating System Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HTGOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HTGOATLOCKOUT-SP
|  |  |  | HWS.OATLO-RST | 25 | deg F | Outdoor Air Temp Low Reset | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OATLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OATLO-RST
|  |  |  | HWS.OATHI-RST | 55 | deg F | Outdoor Air Temp High Reset | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OATHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OATHI-RST
|  |  |  | HWS.FROST-SP2 | 35 | deg F | Outdoor Air Low Limit Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.FROST-SP2 | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.FROST-SP2
|  |  |  | HWS.RADZN-T | 72 | deg F | Radiant Heat Zone Temp (future) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RADZN-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RADZN-T
x |  |  |  | HWS.HWS-SP | 140.4254 | deg F | Heating Water Temp Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWS-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWS-SP
|  |  |  | HWS.RADZN-SP | 68 | deg F | Radiant Heat Zone Setpoint (future) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RADZN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RADZN-SP
|  |  |  | HWS.VLV-MAXPOS | 36.3195 | % | Maximum Position of AHU Valves | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.VLV-MAXPOS | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.VLV-MAXPOS
|  |  |  | HWS.VLVPOS-SP | 5 | % | Valve Position for Pump Shutdown | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.VLVPOS-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.VLVPOS-SP
x |  |  |  | HWS.OA-FLOW | 14203.738 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-FLOW | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-FLOW
x |  |  |  | HWS.MOAD-REQ | 8000 | cfm | Total Minimum Outdoor Air Required | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MOAD-REQ | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MOAD-REQ
x |  |  |  | HWS.CLG-REQ | 99.9981 | % | Maximum Cooling Required | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.CLG-REQ | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.CLG-REQ
|  |  |  | HWS.OA-F1 | 6990.8696 |  | CS Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-F1 | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-F1
|  |  |  | HWS.OA-F2 | 7148.3403 |  | CS Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-F2 | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-F2
|  |  |  | HWS.OA-T | 54.7448 |  | CS Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-T
|  |  |  | HWS.MAD-MAXSP | 100 | % | Output Range High | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MAD-MAXSP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MAD-MAXSP
|  |  |  | HWS.MAD-MINSP | 5 | % | Output Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MAD-MINSP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MAD-MINSP
|  |  |  | HWS.CLG-MAXSP | 100 | % | Input Range High | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.CLG-MAXSP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.CLG-MAXSP
|  |  |  | HWS.CLG-MINSP | 0 | % | Input Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.CLG-MINSP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.CLG-MINSP
|  |  |  | HWS.Restart Delay | 15 | minutes | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.Restart Delay | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.Restart Delay
|  |  |  | HWS.Differential | 2 | deg F | Differential | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.Differential | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.Differential
|  |  |  | HWS.PMPDOWN-TIME | 300 | seconds | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PMPDOWN-TIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PMPDOWN-TIME
|  |  |  | HWS.PHWP-RUNNING | 1 |  | Current Stage | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP-RUNNING | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP-RUNNING
|  |  |  | HWS.PHWP2-RUNTIME | 2139.2 |  | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-RUNTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-RUNTIME
|  |  |  | HWS.PHWP1-RUNTIME | 923.9278 |  | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-RUNTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-RUNTIME
|  |  |  | HWS.HW-SP | 140.4254 | deg F | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HW-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HW-SP
x |  |  |  | HWS.PHWP2-S | Off |  | Primary HW Pump 2 Status | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-S
x |  |  |  | HWS.PHWP1-S | On |  | Primary HW Pump 1 Status | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-S
x |  |  |  | HWS.RAD-C | Open |  | Radiant Heating Valve Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RAD-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RAD-C
x |  |  |  | HWS.PHWP2-C | Off |  | Primary HW Pump 2 Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-C
x |  |  |  | HWS.PHWP1-C | On |  | Primary HW Pump 1 Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-C
x |  |  |  | HWS.SYSTEM-EN | TRUE |  | Heating System Enable | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.SYSTEM-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.SYSTEM-EN
|  |  |  | HWS.PHWP-ROT | FALSE |  | Rotate Lead Pump Now | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP-ROT | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP-ROT
|  |  |  | HWS.TUNING-RESET | FALSE |  | Reset PID Tuning | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.TUNING-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.TUNING-RESET
|  |  |  | HWS.RADHTG-EN | TRUE |  | Radiant Heating Enable | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RADHTG-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RADHTG-EN
|  |  |  | HWS.LOOPFROST-ENABLED | FALSE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.LOOPFROST-ENABLED | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.LOOPFROST-ENABLED
|  |  |  | HWS.HWSYS-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWSYS-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWSYS-AVAILABLE
|  |  |  | HWS.OCC-SCHEDULE | Occupied | 4 | Occupancy Schedule | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OCC-SCHEDULE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OCC-SCHEDULE
|  |  |  | HWS.SYS-RESET | Off | 2 | System Alarm Reset | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.SYS-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.SYS-RESET
|  |  |  | HWS.PHWP2-ALM | Normal | 2 | Pump 2 Lockout Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-ALM | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-ALM
|  |  |  | HWS.PHWP1-ALM | Normal | 2 | Pump 1 Lockout Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-ALM | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-ALM
|  |  |  | HWS.SF-S | On | 2 | Any SF Run Status | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.SF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.SF-S
|  |  |  | HWS.OUTSTATE | Control | 3 | State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OUTSTATE
|  |  |  | HWS.PHWPROTATE-STATE | Idle | 7 | Operating State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWPROTATE-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWPROTATE-STATE
|  |  |  | HWS.PHWP2-OUTSTATE | Off | 2 | Device OnOff | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-OUTSTATE
|  |  |  | HWS.PHWP1-OUTSTATE | On | 2 | Device OnOff | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-OUTSTATE
|  |  |  | HWS.DEVICEPID-STATE | Control | 4 | State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.DEVICEPID-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.DEVICEPID-STATE
|  |  |  | HWS.HWP 2-IA | Normal | 2 | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWP 2-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWP 2-IA
|  |  |  | HWS.HWP 1-IA | Normal | 2 | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWP 1-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWP 1-IA
|  |  |  | HWS | Online |  | HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC004
x | MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC007 | MSF.DA-P | 0.28066 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DA-P
x |  |  |  | MSF.RA-T | 72.4168 | deg F | Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RA-T
x |  |  |  | MSF.DA-T | 73.0233 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DA-T
x |  |  |  | MSF.MSF-O | 60 | % | Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-O
x |  |  |  | MSF.MRF-O | 61.8557 | % | Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-O
x |  |  |  | MSF.CVM-O | 0.39836 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CVM-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CVM-O
|  |  |  | MSF.OA-T | 55.0546 | deg F | Outdoor Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OA-T
|  |  |  | MSF.HTGOATLOCKOUT-SP | 60 | deg F | Heating OA Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.HTGOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.HTGOATLOCKOUT-SP
|  |  |  | MSF.OCC-MINCFM | 4000 | cfm | OA Damper Add for MSF Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OCC-MINCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OCC-MINCFM
x |  |  |  | MSF.DAP-SP | 0.5 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DAP-SP
x |  |  |  | MSF.CLG-O | 99.9981 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-O
x |  |  |  | MSF.MOAD-O | 4000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MOAD-O
|  |  |  | MSF.OCCSPD-SP | 60 | % | Supply Fan Speed Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OCCSPD-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OCCSPD-SP
|  |  |  | MSF.DATHTGMAX-SP | 80 |  | Output Range High | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DATHTGMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DATHTGMAX-SP
|  |  |  | MSF.DATCLGMIN-SP | 60 |  | Output Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DATCLGMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DATCLGMIN-SP
|  |  |  | MSF.OATLO-RST | 40 |  | Input Range High | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OATLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OATLO-RST
|  |  |  | MSF.OATHI-RST | 80 |  | Input Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OATHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OATHI-RST
|  |  |  | MSF.OFFDELAY | 30 | seconds | Off Delay | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OFFDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OFFDELAY
|  |  |  | MSF.ONDELAY | 30 | seconds | On Delay | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.ONDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.ONDELAY
|  |  |  | MSF.OCCMODE-BYPASSTIME | 3600 | seconds | Bypass Time | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OCCMODE-BYPASSTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OCCMODE-BYPASSTIME
|  |  |  | MSF.UNOCC-DIFF | 2 | deg F | Differential | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNOCC-DIFF | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNOCC-DIFF
|  |  |  | MSF.UNOCC-SATTIME | 180 | seconds | Satisfied Timer Duration | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNOCC-SATTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNOCC-SATTIME
|  |  |  | MSF.PFRESTART-TIME | 60 | seconds | Power Fail Restart Time | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.PFRESTART-TIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.PFRESTART-TIME
x |  |  |  | MSF.EFF DA-P | 0.27493 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EFF DA-P
|  |  |  | MSF.RFMAX-SP | 100 | % | Return Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RFMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RFMAX-SP
|  |  |  | MSF.RFMIN-SP | 0 | % | Return Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RFMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RFMIN-SP
|  |  |  | MSF.SFHI-RST | 97 | % | Supply Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SFHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SFHI-RST
|  |  |  | MSF.SFLO-RST | 0 | % | Supply Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SFLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SFLO-RST
|  |  |  | MSF.EMERGENCY DAP-SP | 1.5 | in wc | Emergency Duct Static Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EMERGENCY DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EMERGENCY DAP-SP
|  |  |  | MSF.EMERGENCY SF-O | 70 | % | Emergency On Percent Cmd | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EMERGENCY SF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EMERGENCY SF-O
|  |  |  | MSF.Ramp Rate | 50 | Change per Minute | Ramp Rate | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.Ramp Rate | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.Ramp Rate
|  |  |  | MSF.Fan Run Speed | 60 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.Fan Run Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.Fan Run Speed
|  |  |  | MSF.OALT-SP | 41 | deg F | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OALT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OALT-SP
x |  |  |  | MSF.EFFDAT-SP | 72.4727 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EFFDAT-SP
|  |  |  | MSF.DATCLGUNOCC-SP | 55 | deg F | Unocc Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DATCLGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DATCLGUNOCC-SP
|  |  |  | MSF.DATHTGUNOCC-SP | 90 | deg F | Unocc Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DATHTGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DATHTGUNOCC-SP
|  |  |  | MSF.MAD-RAMPRATE | 50 | Change per Minute | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MAD-RAMPRATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MAD-RAMPRATE
x |  |  |  | MSF.MSF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-S
x |  |  |  | MSF.MRF-S | On |  | Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-S
|  |  |  | MSF.LT-A | Normal |  | Low Temperature Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.LT-A | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.LT-A
x |  |  |  | MSF.MSF-C | On |  | Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-C
x |  |  |  | MSF.MRF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-C
|  |  |  | MSF.RFISO-C | Open |  | Return Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RFISO-C
|  |  |  | MSF.SFISO-C | Open |  | Supply Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SFISO-C
|  |  |  | MSF.CLG-EN | TRUE |  | Cooling is Available | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-EN
|  |  |  | MSF.TUNING-RESET | FALSE |  | Reset PID Tuning | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.TUNING-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.TUNING-RESET
|  |  |  | MSF.CLG-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-AVAILABLE
|  |  |  | MSF.RH-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RH-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RH-AVAILABLE
|  |  |  | MSF.PFRESTART-EN | TRUE |  | Power Fail Restart Enable | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.PFRESTART-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.PFRESTART-EN
|  |  |  | MSF.RF-Enabled | TRUE |  | Device Enable | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RF-Enabled | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RF-Enabled
|  |  |  | MSF.WC-C | Normal |  | Warmup/Cooldown Mode | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.WC-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.WC-C
|  |  |  | MSF.UNITEN-MODE | Enable |  | Unit Enable Mode | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNITEN-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNITEN-MODE
|  |  |  | MSF.SYS-RESET | Off |  | System Alarm Reset | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SYS-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SYS-RESET
|  |  |  | MSF.OCC-SCHEDULE | Occupied |  | Occupancy from Schedule | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OCC-SCHEDULE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OCC-SCHEDULE
|  |  |  | MSF.APP-MODE | Auto |  | Application Mode | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.APP-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.APP-MODE
|  |  |  | MSF.OUTSTATE | Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OUTSTATE
|  |  |  | MSF.DELAYTYPE | Off |  | Delay Type | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DELAYTYPE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DELAYTYPE
|  |  |  | MSF.AHU-STATE | HX Cool+Mech |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.AHU-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.AHU-STATE
|  |  |  | MSF.EFF-OCC | Occupied |  | Effective Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EFF-OCC | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EFF-OCC
|  |  |  | MSF.UNOCC-STATE | Unocc Cntrl Not Req'd |  | Unocc Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNOCC-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNOCC-STATE
|  |  |  | MSF.UNITEN-STATE | Enable |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNITEN-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNITEN-STATE
|  |  |  | MSF.STARTSTOP-STATE | On |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.STARTSTOP-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.STARTSTOP-STATE
|  |  |  | MSF.NOFLOW-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.NOFLOW-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.NOFLOW-STATE
|  |  |  | MSF.SMOKE SEQUENCE-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SMOKE SEQUENCE-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SMOKE SEQUENCE-STATE
|  |  |  | MSF.RF-OUTSTATE | Fan Track Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RF-OUTSTATE
|  |  |  | MSF.SF-OUTSTATE | Ramp |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SF-OUTSTATE
|  |  |  | MSF.RF-IA | Normal |  | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RF-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RF-IA
|  |  |  | MSF.RF-Status | On |  | Device Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RF-Status | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RF-Status
|  |  |  | MSF.RH-OUTSTATE | Off |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RH-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RH-OUTSTATE
|  |  |  | MSF.CLG-OUTSTATE | T Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-OUTSTATE
|  |  |  | MSF.MAD-OUTSTATE | Min OA |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MAD-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MAD-OUTSTATE
|  |  |  | MSF | Online |  | MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC007
x | ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC010 | ASF.DA-P | 0.001469 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DA-P
x |  |  |  | ASF.RA-T | 69.4183 | deg F | Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RA-T
x |  |  |  | ASF.RA-Q | 443.8686 | ppm | Return Air Quality | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RA-Q | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RA-Q
x |  |  |  | ASF.DA-T | 92.0338 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DA-T
x |  |  |  | ASF.ZN-T | 70.7348 | deg F | Zone Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZN-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZN-T
x |  |  |  | ASF.ASF-O | 40 | % | Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-O
x |  |  |  | ASF.ARF-O | 40 | % | Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-O
x |  |  |  | ASF.CVA-O | 0.1055 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CVA-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CVA-O
|  |  |  | ASF.WC-ADJ | 0 | deg F | Warmer/Cooler Adjust | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.WC-ADJ | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.WC-ADJ
|  |  |  | ASF.OA-T | 54.7565 | deg F | Outdoor Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OA-T
|  |  |  | ASF.HTGOATLOCKOUT-SP | 60 | deg F | Heating OA Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.HTGOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.HTGOATLOCKOUT-SP
|  |  |  | ASF.OCC-MINCFM | 2000 | cfm | OA Damper Add for ASF Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCC-MINCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCC-MINCFM
x |  |  |  | ASF.DAP-SP | 0.4 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DAP-SP
x |  |  |  | ASF.ZNT-SP | 72 | deg F | Zone Temperature Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZNT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZNT-SP
x |  |  |  | ASF.CLG-O | 100 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-O
x |  |  |  | ASF.RAQ-SP | 520 | ppm | Return Air CO2 Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RAQ-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RAQ-SP
x |  |  |  | ASF.MOAD-O | 2000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MOAD-O
|  |  |  | ASF.OCC-MAXCFM | 0 | cfm | OA Damper Add for ASF Max CO2 | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCC-MAXCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCC-MAXCFM
|  |  |  | ASF.OFFDELAY | 30 | seconds | Off Delay | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OFFDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OFFDELAY
|  |  |  | ASF.ONDELAY | 30 | seconds | On Delay | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ONDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ONDELAY
|  |  |  | ASF.Stageup Interval | 10 | minutes | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Stageup Interval | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Stageup Interval
|  |  |  | ASF.Fan Stage 4 Speed | 73 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Stage 4 Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Stage 4 Speed
|  |  |  | ASF.Fan Stage 3 Speed | 63 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Stage 3 Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Stage 3 Speed
|  |  |  | ASF.Fan Stage 1 Speed (Min)40 | 40 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Stage 1 Speed (Min)40 | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Stage 1 Speed (Min)
|  |  |  | ASF.Fan Stage 2 Speed(48.3) | 50 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Stage 2 Speed(48.3) | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Stage 2 Speed
|  |  |  | ASF.Setpoint Differential | 50 | ppm | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Setpoint Differential | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Setpoint Differential
|  |  |  | ASF.Stagedown Interval | 10 | minutes | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Stagedown Interval | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Stagedown Interval
|  |  |  | ASF.OCCMODE-BYPASSTIME | 3600 | seconds | Bypass Time | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCCMODE-BYPASSTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCCMODE-BYPASSTIME
|  |  |  | ASF.UNOCC-DIFF | 2 | deg F | Differential | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNOCC-DIFF | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNOCC-DIFF
|  |  |  | ASF.UNOCC-SATTIME | 180 | seconds | Satisfied Timer Duration | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNOCC-SATTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNOCC-SATTIME
|  |  |  | ASF.PFRESTART-TIME | 60 | seconds | Power Fail Restart Time | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.PFRESTART-TIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.PFRESTART-TIME
x |  |  |  | ASF.EFF DA-P | 0.0013646 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFF DA-P
|  |  |  | ASF.EFFHTG-SP | 72 | deg F | Effective Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFFHTG-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFFHTG-SP
|  |  |  | ASF.EFFCLG-SP | 72 | deg F | Effective Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFFCLG-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFFCLG-SP
|  |  |  | ASF.HTGUNOCC-SP | 65 | deg F | Unocc Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.HTGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.HTGUNOCC-SP
|  |  |  | ASF.HTGSTBY-SP | 68 | deg F | Standby Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.HTGSTBY-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.HTGSTBY-SP
|  |  |  | ASF.HTGOCC-SP | 70 | deg F | Occ Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.HTGOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.HTGOCC-SP
|  |  |  | ASF.CLGUNOCC-SP | 82 | deg F | Unocc Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLGUNOCC-SP
|  |  |  | ASF.CLGSTBY-SP | 77 | deg F | Standby Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLGSTBY-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLGSTBY-SP
|  |  |  | ASF.CLGOCC-SP | 70 | deg F | Occ Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLGOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLGOCC-SP
|  |  |  | ASF.RFMAX-SP | 100 | % | Return Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RFMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RFMAX-SP
|  |  |  | ASF.RFMIN-SP | 0 | % | Return Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RFMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RFMIN-SP
|  |  |  | ASF.SFHI-RST | 100 | % | Supply Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SFHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SFHI-RST
|  |  |  | ASF.SFLO-RST | 0 | % | Supply Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SFLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SFLO-RST
|  |  |  | ASF.EMERGENCY DAP-SP | 1.5 | in wc | Emergency Duct Static Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EMERGENCY DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EMERGENCY DAP-SP
|  |  |  | ASF.EMERGENCY SF-O | 70 | % | Emergency On Percent Cmd | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EMERGENCY SF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EMERGENCY SF-O
|  |  |  | ASF.Ramp Rate | 50 | Change per Minute | Ramp Rate | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Ramp Rate | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Ramp Rate
|  |  |  | ASF.Fan Run Speed | 40 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Run Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Run Speed
|  |  |  | ASF.OALT-SP | 41 | deg F | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OALT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OALT-SP
x |  |  |  | ASF.EFFDAT-SP | 90 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFFDAT-SP
|  |  |  | ASF.DATCLGUNOCC-SP | 55 | deg F | Unocc Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATCLGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATCLGUNOCC-SP
|  |  |  | ASF.DATHTGUNOCC-SP | 90 | deg F | Unocc Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATHTGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATHTGUNOCC-SP
|  |  |  | ASF.MAD-RAMPRATE | 50 | Change per Minute | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MAD-RAMPRATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MAD-RAMPRATE
|  |  |  | ASF.RACO2HI-RST | 1000 | ppm | CO2 Reset B | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RACO2HI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RACO2HI-RST
|  |  |  | ASF.MAD-MINPOS | 2000 | % | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MAD-MINPOS | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MAD-MINPOS
|  |  |  | ASF.DATCLGMIN-SP | 55 | deg F | Discharge Air Setpoint Cooling Min | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATCLGMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATCLGMIN-SP
|  |  |  | ASF.DATSATISFIED-SP | 70 | deg F | Discharge Air Setpoint Zone Satisfied | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATSATISFIED-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATSATISFIED-SP
|  |  |  | ASF.DATHTGMAX-SP | 90 | deg F | Discharge Air Setpoint Heating Max | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATHTGMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATHTGMAX-SP
x |  |  |  | ASF.ASF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-S
x |  |  |  | ASF.ARF-S | On |  | Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-S
|  |  |  | ASF.LT-A | Normal |  | Low Temperature Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.LT-A | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.LT-A
x |  |  |  | ASF.ASF-C | On |  | Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-C
x |  |  |  | ASF.ARF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-C
|  |  |  | ASF.RFISO-C | Open |  | Return Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RFISO-C
|  |  |  | ASF.SFISO-C | Open |  | Supply Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SFISO-C
|  |  |  | ASF.ZN-TOCC | Inactive |  | Zone Temporary Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZN-TOCC | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZN-TOCC
|  |  |  | ASF.CLG-EN | TRUE |  | Cooling is Available | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-EN
|  |  |  | ASF.TUNING-RESET | FALSE |  | Reset PID Tuning | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.TUNING-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.TUNING-RESET
|  |  |  | ASF.CLG-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-AVAILABLE
|  |  |  | ASF.RH-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RH-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RH-AVAILABLE
|  |  |  | ASF.PFRESTART-EN | TRUE |  | Power Fail Restart Enable | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.PFRESTART-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.PFRESTART-EN
|  |  |  | ASF.RF-Enabled | TRUE |  | Device Enable | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RF-Enabled | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RF-Enabled
|  |  |  | ASF.OCC-MODE | Occupied |  | Occupancy Status Display | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCC-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCC-MODE
|  |  |  | ASF.WC-C | Normal |  | Warmup/Cooldown Mode | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.WC-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.WC-C
|  |  |  | ASF.UNITEN-MODE | Enable |  | Unit Enable Mode | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNITEN-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNITEN-MODE
|  |  |  | ASF.SYS-RESET | Off |  | System Alarm Reset | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SYS-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SYS-RESET
|  |  |  | ASF.OCC-SCHEDULE | Occupied |  | Occupancy from Schedule | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCC-SCHEDULE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCC-SCHEDULE
|  |  |  | ASF.APP-MODE | Auto |  | Application Mode | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.APP-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.APP-MODE
|  |  |  | ASF.DELAYTYPE | Off |  | Delay Type | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DELAYTYPE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DELAYTYPE
|  |  |  | ASF.AHU-STATE | HX Cool+Mech |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.AHU-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.AHU-STATE
|  |  |  | ASF.ZNT-STATE | Heating |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZNT-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZNT-STATE
|  |  |  | ASF.EFF-OCC | Occupied |  | Effective Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFF-OCC | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFF-OCC
|  |  |  | ASF.UNOCC-STATE | Unocc Cntrl Not Req'd |  | Unocc Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNOCC-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNOCC-STATE
|  |  |  | ASF.UNITEN-STATE | Enable |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNITEN-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNITEN-STATE
|  |  |  | ASF.STARTSTOP-STATE | On |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.STARTSTOP-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.STARTSTOP-STATE
|  |  |  | ASF.NOFLOW-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.NOFLOW-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.NOFLOW-STATE
|  |  |  | ASF.SMOKE SEQUENCE-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SMOKE SEQUENCE-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SMOKE SEQUENCE-STATE
|  |  |  | ASF.RF-OUTSTATE | Fan Track Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RF-OUTSTATE
|  |  |  | ASF.SF-OUTSTATE | Ramp |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SF-OUTSTATE
|  |  |  | ASF.RF-IA | Normal |  | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RF-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RF-IA
|  |  |  | ASF.RF-Status | On |  | Device Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RF-Status | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RF-Status
|  |  |  | ASF.RH-OUTSTATE | Off |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RH-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RH-OUTSTATE
|  |  |  | ASF.CLG-OUTSTATE | T Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-OUTSTATE
|  |  |  | ASF.MAD-OUTSTATE | Min OA |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MAD-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MAD-OUTSTATE
|  |  |  | ASF.DATSP-STATE | Heating DA-T Reset |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATSP-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATSP-STATE
|  |  |  | ASF | Online |  | ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC010
x | LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC013 | LSF.DA-P | 0.07192 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DA-P
x |  |  |  | LSF.MA-T | 55.9926 | deg F | Mixed Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MA-T
x |  |  |  | LSF.DA-T | 73.0527 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DA-T
x |  |  |  | LSF.OA-F2 | 6939.207 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-F2 | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-F2
x |  |  |  | LSF.OA-F1 | 7046.188 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-F1 | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-F1
x |  |  |  | LSF.LRA-T | 71.1619 | deg F | Library Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRA-T
x |  |  |  | LSF.OA-T | 54.3803 | deg F | Outdoor Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-T
x |  |  |  | LSF.LSF-O | 50 | % | Library Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-O
x |  |  |  | LSF.CVL-O | 37.4286 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CVL-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CVL-O
x |  |  |  | LSF.LRF-O | 62 | % | Library Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-O
|  |  |  | LSF.HTGOATLOCKOUT-SP | 60 | deg F | Heating OA Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.HTGOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.HTGOATLOCKOUT-SP
|  |  |  | LSF.OCC-MINCFM | 2000 | cfm | OA Damper Add for LSF Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OCC-MINCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OCC-MINCFM
x |  |  |  | LSF.DAP-SP | 0.2 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DAP-SP
x |  |  |  | LSF.CLG-O | 0 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-O
x |  |  |  | LSF.MOAD-O | 2000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MOAD-O
|  |  |  | LSF.OCCSPD-SP | 50 | % | Occupied Supply Fan Speed Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OCCSPD-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OCCSPD-SP
|  |  |  | LSF.UNOCSPD-SP | 30 | % | Unoccupied Supply Fan Speed Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOCSPD-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOCSPD-SP
|  |  |  | LSF.UNOC-MINCFM | 2000 | cfm | OA Damper Add for LSF Unoccupied | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOC-MINCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOC-MINCFM
|  |  |  | LSF.DATHTGMAX-SP | 90 |  | Output Range High | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DATHTGMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DATHTGMAX-SP
|  |  |  | LSF.DATCLGMIN-SP | 55 |  | Output Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DATCLGMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DATCLGMIN-SP
|  |  |  | LSF.OATLO-RST | 30 |  | Input Range High | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OATLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OATLO-RST
|  |  |  | LSF.OATHI-RST | 80 |  | Input Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OATHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OATHI-RST
|  |  |  | LSF.OFFDELAY | 30 | seconds | Off Delay | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OFFDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OFFDELAY
|  |  |  | LSF.ONDELAY | 30 | seconds | On Delay | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.ONDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.ONDELAY
|  |  |  | LSF.OCCMODE-BYPASSTIME | 3600 | seconds | Bypass Time | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OCCMODE-BYPASSTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OCCMODE-BYPASSTIME
|  |  |  | LSF.UNOCC-DIFF | 2 | deg F | Differential | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOCC-DIFF | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOCC-DIFF
|  |  |  | LSF.UNOCC-SATTIME | 180 | seconds | Satisfied Timer Duration | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOCC-SATTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOCC-SATTIME
|  |  |  | LSF.PFRESTART-TIME | 60 | seconds | Power Fail Restart Time | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.PFRESTART-TIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.PFRESTART-TIME
x |  |  |  | LSF.EFF DA-P | 0.072259 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EFF DA-P
|  |  |  | LSF.RFMAX-SP | 124 | % | Return Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RFMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RFMAX-SP
|  |  |  | LSF.RFMIN-SP | 0 | % | Return Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RFMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RFMIN-SP
|  |  |  | LSF.SFHI-RST | 100 | % | Supply Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SFHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SFHI-RST
|  |  |  | LSF.SFLO-RST | 0 | % | Supply Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SFLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SFLO-RST
|  |  |  | LSF.EMERGENCY DAP-SP | 1.5 | in wc | Emergency Duct Static Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EMERGENCY DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EMERGENCY DAP-SP
|  |  |  | LSF.EMERGENCY SF-O | 70 | % | Emergency On Percent Cmd | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EMERGENCY SF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EMERGENCY SF-O
|  |  |  | LSF.Ramp Rate | 50 | Change per Minute | Ramp Rate | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.Ramp Rate | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.Ramp Rate
|  |  |  | LSF.Fan Run Speed | 50 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.Fan Run Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.Fan Run Speed
|  |  |  | LSF.OALT-SP | 41 | deg F | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OALT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OALT-SP
x |  |  |  | LSF.EFFDAT-SP | 73.0077 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EFFDAT-SP
|  |  |  | LSF.DATCLGUNOCC-SP | 55 | deg F | Unocc Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DATCLGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DATCLGUNOCC-SP
|  |  |  | LSF.DATHTGUNOCC-SP | 90 | deg F | Unocc Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DATHTGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DATHTGUNOCC-SP
|  |  |  | LSF.MAD-RAMPRATE | 50 | Change per Minute | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MAD-RAMPRATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MAD-RAMPRATE
x |  |  |  | LSF.LSF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-S
|  |  |  | LSF.LT-A | Normal |  | Low Temperature Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LT-A | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LT-A
x |  |  |  | LSF.LRF-S | On |  | Library Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-S
x |  |  |  | LSF.TEF-S | On |  | Toilet Exhaust Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.TEF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.TEF-S
x |  |  |  | LSF.LSF-C | On |  | Library Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-C
|  |  |  | LSF.LRFISO-C | Open |  | Library Return Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRFISO-C
x |  |  |  | LSF.TEF-C | On |  | Toilet Exhaust Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.TEF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.TEF-C
x |  |  |  | LSF.LRF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-C
|  |  |  | LSF.SFISO-C | Open |  | Supply Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SFISO-C
|  |  |  | LSF.CLG-EN | TRUE |  | Cooling is Available | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-EN
|  |  |  | LSF.TUNING-RESET | FALSE |  | Reset PID Tuning | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.TUNING-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.TUNING-RESET
|  |  |  | LSF.CLG-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-AVAILABLE
|  |  |  | LSF.RH-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RH-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RH-AVAILABLE
|  |  |  | LSF.PFRESTART-EN | TRUE |  | Power Fail Restart Enable | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.PFRESTART-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.PFRESTART-EN
|  |  |  | LSF.RF-Enabled | TRUE |  | Device Enable | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RF-Enabled | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RF-Enabled
|  |  |  | LSF.WC-C | Normal |  | Warmup/Cooldown Mode | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.WC-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.WC-C
|  |  |  | LSF.UNITEN-MODE | Enable |  | Unit Enable Mode | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNITEN-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNITEN-MODE
|  |  |  | LSF.SYS-RESET | Reset |  | System Alarm Reset | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SYS-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SYS-RESET
|  |  |  | LSF.OCC-SCHEDULE | Occupied |  | Occupancy from Schedule | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OCC-SCHEDULE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OCC-SCHEDULE
|  |  |  | LSF.APP-MODE | Auto |  | Application Mode | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.APP-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.APP-MODE
|  |  |  | LSF.OUTSTATE | Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OUTSTATE
|  |  |  | LSF.DELAYTYPE | Off |  | Delay Type | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DELAYTYPE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DELAYTYPE
|  |  |  | LSF.AHU-STATE | HX Heat+Preheat+Reheat |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.AHU-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.AHU-STATE
|  |  |  | LSF.EFF-OCC | Occupied |  | Effective Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EFF-OCC | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EFF-OCC
|  |  |  | LSF.UNOCC-STATE | Unocc Cntrl Not Req'd |  | Unocc Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOCC-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOCC-STATE
|  |  |  | LSF.UNITEN-STATE | Enable |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNITEN-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNITEN-STATE
|  |  |  | LSF.STARTSTOP-STATE | On |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.STARTSTOP-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.STARTSTOP-STATE
|  |  |  | LSF.NOFLOW-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.NOFLOW-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.NOFLOW-STATE
|  |  |  | LSF.SMOKE SEQUENCE-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SMOKE SEQUENCE-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SMOKE SEQUENCE-STATE
|  |  |  | LSF.RF-OUTSTATE | Fan Track Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RF-OUTSTATE
|  |  |  | LSF.SF-OUTSTATE | Ramp |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SF-OUTSTATE
|  |  |  | LSF.RF-IA | Normal |  | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RF-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RF-IA
|  |  |  | LSF.RF-Status | On |  | Device Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RF-Status | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RF-Status
|  |  |  | LSF.RH-OUTSTATE | T Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RH-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RH-OUTSTATE
|  |  |  | LSF.CLG-OUTSTATE | Off |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-OUTSTATE
|  |  |  | LSF.MAD-OUTSTATE | Min OA |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MAD-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MAD-OUTSTATE
|  |  |  | LSF | Online |  | LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC013
x | MSF-VFD | UW-EMS-OPS>GOWEN HALL>FC-1>MSF-VFD | FAC-JCIDB1:UW-NAE90/FC-1.MSF-VFD | Power [KW] | 1.82 | kW | Actual motor power in KW - P1610 | UW-EMS-OPS>GOWEN HALL>FC-1>MSF-VFD>Power [KW] | FAC-JCIDB1:UW-NAE90/FC-1.MSF-VFD.AV-15

## Sheet2
Controller Information |  |  | Points
Description | Location |  | Name/Label | Value | Units/States | Description | Location
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC004 | HWS.DHWS-T | 116.3815 | deg F | Domestic HW Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.DHWS-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.DHWS-T
|  |  | HWS.PHWS-T | 140.6453 | deg F | Primary HW Supply Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWS-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWS-T
|  |  | HWS.PHWR-T | 132.2234 | deg F | Primary HW Return Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWR-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWR-T
|  |  | HWS.HX1V2-O | 0.54986 | % | Heat Exchanger 1 Valve 2 Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HX1V2-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HX1V2-O
|  |  | HWS.HX1V1-O | 58.6363 | % | Heat Exchanger 1 Valve 1 Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HX1V1-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HX1V1-O
|  |  | HWS.MAD-O | 99.9982 | % | Mixed Air Damper Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MAD-O
|  |  | HWS.RADOATLOCKOUT-SP | 60 | deg F | Radiant Heating Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RADOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RADOATLOCKOUT-SP
|  |  | HWS.HWMAX-SP | 190 | deg F | Maximum HW Temp Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWMAX-SP
|  |  | HWS.HWMIN-SP | 140 | deg F | Minimum HW Temp Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWMIN-SP
|  |  | HWS.HTGOATLOCKOUT-SP | 65 | deg F | Heating System Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HTGOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HTGOATLOCKOUT-SP
|  |  | HWS.OATLO-RST | 25 | deg F | Outdoor Air Temp Low Reset | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OATLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OATLO-RST
|  |  | HWS.OATHI-RST | 55 | deg F | Outdoor Air Temp High Reset | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OATHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OATHI-RST
|  |  | HWS.FROST-SP2 | 35 | deg F | Outdoor Air Low Limit Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.FROST-SP2 | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.FROST-SP2
|  |  | HWS.RADZN-T | 72 | deg F | Radiant Heat Zone Temp (future) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RADZN-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RADZN-T
|  |  | HWS.HWS-SP | 140.4254 | deg F | Heating Water Temp Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWS-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWS-SP
|  |  | HWS.RADZN-SP | 68 | deg F | Radiant Heat Zone Setpoint (future) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RADZN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RADZN-SP
|  |  | HWS.VLV-MAXPOS | 36.3195 | % | Maximum Position of AHU Valves | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.VLV-MAXPOS | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.VLV-MAXPOS
|  |  | HWS.VLVPOS-SP | 5 | % | Valve Position for Pump Shutdown | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.VLVPOS-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.VLVPOS-SP
|  |  | HWS.OA-FLOW | 14203.738 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-FLOW | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-FLOW
|  |  | HWS.MOAD-REQ | 8000 | cfm | Total Minimum Outdoor Air Required | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MOAD-REQ | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MOAD-REQ
|  |  | HWS.CLG-REQ | 99.9981 | % | Maximum Cooling Required | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.CLG-REQ | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.CLG-REQ
|  |  | HWS.OA-F1 | 6990.8696 |  | CS Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-F1 | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-F1
|  |  | HWS.OA-F2 | 7148.3403 |  | CS Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-F2 | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-F2
|  |  | HWS.OA-T | 54.7448 |  | CS Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-T
|  |  | HWS.MAD-MAXSP | 100 | % | Output Range High | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MAD-MAXSP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MAD-MAXSP
|  |  | HWS.MAD-MINSP | 5 | % | Output Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MAD-MINSP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MAD-MINSP
|  |  | HWS.CLG-MAXSP | 100 | % | Input Range High | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.CLG-MAXSP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.CLG-MAXSP
|  |  | HWS.CLG-MINSP | 0 | % | Input Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.CLG-MINSP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.CLG-MINSP
|  |  | HWS.Restart Delay | 15 | minutes | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.Restart Delay | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.Restart Delay
|  |  | HWS.Differential | 2 | deg F | Differential | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.Differential | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.Differential
|  |  | HWS.PMPDOWN-TIME | 300 | seconds | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PMPDOWN-TIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PMPDOWN-TIME
|  |  | HWS.PHWP-RUNNING | 1 |  | Current Stage | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP-RUNNING | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP-RUNNING
|  |  | HWS.PHWP2-RUNTIME | 2139.2 |  | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-RUNTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-RUNTIME
|  |  | HWS.PHWP1-RUNTIME | 923.9278 |  | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-RUNTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-RUNTIME
|  |  | HWS.HW-SP | 140.4254 | deg F | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HW-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HW-SP
|  |  | HWS.PHWP2-S | Off |  | Primary HW Pump 2 Status | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-S
|  |  | HWS.PHWP1-S | On |  | Primary HW Pump 1 Status | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-S
|  |  | HWS.RAD-C | Open |  | Radiant Heating Valve Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RAD-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RAD-C
|  |  | HWS.PHWP2-C | Off |  | Primary HW Pump 2 Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-C
|  |  | HWS.PHWP1-C | On |  | Primary HW Pump 1 Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-C
|  |  | HWS.SYSTEM-EN | TRUE |  | Heating System Enable | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.SYSTEM-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.SYSTEM-EN
|  |  | HWS.PHWP-ROT | FALSE |  | Rotate Lead Pump Now | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP-ROT | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP-ROT
|  |  | HWS.TUNING-RESET | FALSE |  | Reset PID Tuning | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.TUNING-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.TUNING-RESET
|  |  | HWS.RADHTG-EN | TRUE |  | Radiant Heating Enable | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RADHTG-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RADHTG-EN
|  |  | HWS.LOOPFROST-ENABLED | FALSE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.LOOPFROST-ENABLED | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.LOOPFROST-ENABLED
|  |  | HWS.HWSYS-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWSYS-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWSYS-AVAILABLE
|  |  | HWS.OCC-SCHEDULE | Occupied | 4 | Occupancy Schedule | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OCC-SCHEDULE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OCC-SCHEDULE
|  |  | HWS.SYS-RESET | Off | 2 | System Alarm Reset | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.SYS-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.SYS-RESET
|  |  | HWS.PHWP2-ALM | Normal | 2 | Pump 2 Lockout Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-ALM | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-ALM
|  |  | HWS.PHWP1-ALM | Normal | 2 | Pump 1 Lockout Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-ALM | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-ALM
|  |  | HWS.SF-S | On | 2 | Any SF Run Status | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.SF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.SF-S
|  |  | HWS.OUTSTATE | Control | 3 | State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OUTSTATE
|  |  | HWS.PHWPROTATE-STATE | Idle | 7 | Operating State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWPROTATE-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWPROTATE-STATE
|  |  | HWS.PHWP2-OUTSTATE | Off | 2 | Device OnOff | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-OUTSTATE
|  |  | HWS.PHWP1-OUTSTATE | On | 2 | Device OnOff | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-OUTSTATE
|  |  | HWS.DEVICEPID-STATE | Control | 4 | State | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.DEVICEPID-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.DEVICEPID-STATE
|  |  | HWS.HWP 2-IA | Normal | 2 | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWP 2-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWP 2-IA
|  |  | HWS.HWP 1-IA | Normal | 2 | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWP 1-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWP 1-IA
|  |  | HWS | Online |  | HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC004
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC007 | MSF.DA-P | 0.28066 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DA-P
|  |  | MSF.RA-T | 72.4168 | deg F | Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RA-T
|  |  | MSF.DA-T | 73.0233 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DA-T
|  |  | MSF.MSF-O | 60 | % | Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-O
|  |  | MSF.MRF-O | 61.8557 | % | Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-O
|  |  | MSF.CVM-O | 0.39836 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CVM-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CVM-O
|  |  | MSF.OA-T | 55.0546 | deg F | Outdoor Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OA-T
|  |  | MSF.HTGOATLOCKOUT-SP | 60 | deg F | Heating OA Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.HTGOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.HTGOATLOCKOUT-SP
|  |  | MSF.OCC-MINCFM | 4000 | cfm | OA Damper Add for MSF Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OCC-MINCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OCC-MINCFM
|  |  | MSF.DAP-SP | 0.5 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DAP-SP
|  |  | MSF.CLG-O | 99.9981 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-O
|  |  | MSF.MOAD-O | 4000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MOAD-O
|  |  | MSF.OCCSPD-SP | 60 | % | Supply Fan Speed Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OCCSPD-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OCCSPD-SP
|  |  | MSF.DATHTGMAX-SP | 80 |  | Output Range High | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DATHTGMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DATHTGMAX-SP
|  |  | MSF.DATCLGMIN-SP | 60 |  | Output Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DATCLGMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DATCLGMIN-SP
|  |  | MSF.OATLO-RST | 40 |  | Input Range High | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OATLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OATLO-RST
|  |  | MSF.OATHI-RST | 80 |  | Input Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OATHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OATHI-RST
|  |  | MSF.OFFDELAY | 30 | seconds | Off Delay | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OFFDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OFFDELAY
|  |  | MSF.ONDELAY | 30 | seconds | On Delay | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.ONDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.ONDELAY
|  |  | MSF.OCCMODE-BYPASSTIME | 3600 | seconds | Bypass Time | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OCCMODE-BYPASSTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OCCMODE-BYPASSTIME
|  |  | MSF.UNOCC-DIFF | 2 | deg F | Differential | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNOCC-DIFF | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNOCC-DIFF
|  |  | MSF.UNOCC-SATTIME | 180 | seconds | Satisfied Timer Duration | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNOCC-SATTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNOCC-SATTIME
|  |  | MSF.PFRESTART-TIME | 60 | seconds | Power Fail Restart Time | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.PFRESTART-TIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.PFRESTART-TIME
|  |  | MSF.EFF DA-P | 0.27493 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EFF DA-P
|  |  | MSF.RFMAX-SP | 100 | % | Return Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RFMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RFMAX-SP
|  |  | MSF.RFMIN-SP | 0 | % | Return Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RFMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RFMIN-SP
|  |  | MSF.SFHI-RST | 97 | % | Supply Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SFHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SFHI-RST
|  |  | MSF.SFLO-RST | 0 | % | Supply Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SFLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SFLO-RST
|  |  | MSF.EMERGENCY DAP-SP | 1.5 | in wc | Emergency Duct Static Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EMERGENCY DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EMERGENCY DAP-SP
|  |  | MSF.EMERGENCY SF-O | 70 | % | Emergency On Percent Cmd | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EMERGENCY SF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EMERGENCY SF-O
|  |  | MSF.Ramp Rate | 50 | Change per Minute | Ramp Rate | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.Ramp Rate | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.Ramp Rate
|  |  | MSF.Fan Run Speed | 60 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.Fan Run Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.Fan Run Speed
|  |  | MSF.OALT-SP | 41 | deg F | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OALT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OALT-SP
|  |  | MSF.EFFDAT-SP | 72.4727 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EFFDAT-SP
|  |  | MSF.DATCLGUNOCC-SP | 55 | deg F | Unocc Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DATCLGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DATCLGUNOCC-SP
|  |  | MSF.DATHTGUNOCC-SP | 90 | deg F | Unocc Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DATHTGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DATHTGUNOCC-SP
|  |  | MSF.MAD-RAMPRATE | 50 | Change per Minute | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MAD-RAMPRATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MAD-RAMPRATE
|  |  | MSF.MSF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-S
|  |  | MSF.MRF-S | On |  | Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-S
|  |  | MSF.LT-A | Normal |  | Low Temperature Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.LT-A | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.LT-A
|  |  | MSF.MSF-C | On |  | Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-C
|  |  | MSF.MRF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-C
|  |  | MSF.RFISO-C | Open |  | Return Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RFISO-C
|  |  | MSF.SFISO-C | Open |  | Supply Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SFISO-C
|  |  | MSF.CLG-EN | TRUE |  | Cooling is Available | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-EN
|  |  | MSF.TUNING-RESET | FALSE |  | Reset PID Tuning | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.TUNING-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.TUNING-RESET
|  |  | MSF.CLG-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-AVAILABLE
|  |  | MSF.RH-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RH-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RH-AVAILABLE
|  |  | MSF.PFRESTART-EN | TRUE |  | Power Fail Restart Enable | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.PFRESTART-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.PFRESTART-EN
|  |  | MSF.RF-Enabled | TRUE |  | Device Enable | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RF-Enabled | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RF-Enabled
|  |  | MSF.WC-C | Normal |  | Warmup/Cooldown Mode | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.WC-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.WC-C
|  |  | MSF.UNITEN-MODE | Enable |  | Unit Enable Mode | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNITEN-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNITEN-MODE
|  |  | MSF.SYS-RESET | Off |  | System Alarm Reset | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SYS-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SYS-RESET
|  |  | MSF.OCC-SCHEDULE | Occupied |  | Occupancy from Schedule | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OCC-SCHEDULE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OCC-SCHEDULE
|  |  | MSF.APP-MODE | Auto |  | Application Mode | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.APP-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.APP-MODE
|  |  | MSF.OUTSTATE | Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.OUTSTATE
|  |  | MSF.DELAYTYPE | Off |  | Delay Type | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DELAYTYPE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DELAYTYPE
|  |  | MSF.AHU-STATE | HX Cool+Mech |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.AHU-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.AHU-STATE
|  |  | MSF.EFF-OCC | Occupied |  | Effective Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EFF-OCC | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EFF-OCC
|  |  | MSF.UNOCC-STATE | Unocc Cntrl Not Req'd |  | Unocc Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNOCC-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNOCC-STATE
|  |  | MSF.UNITEN-STATE | Enable |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.UNITEN-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.UNITEN-STATE
|  |  | MSF.STARTSTOP-STATE | On |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.STARTSTOP-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.STARTSTOP-STATE
|  |  | MSF.NOFLOW-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.NOFLOW-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.NOFLOW-STATE
|  |  | MSF.SMOKE SEQUENCE-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SMOKE SEQUENCE-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SMOKE SEQUENCE-STATE
|  |  | MSF.RF-OUTSTATE | Fan Track Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RF-OUTSTATE
|  |  | MSF.SF-OUTSTATE | Ramp |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.SF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.SF-OUTSTATE
|  |  | MSF.RF-IA | Normal |  | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RF-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RF-IA
|  |  | MSF.RF-Status | On |  | Device Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RF-Status | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RF-Status
|  |  | MSF.RH-OUTSTATE | Off |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RH-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RH-OUTSTATE
|  |  | MSF.CLG-OUTSTATE | T Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-OUTSTATE
|  |  | MSF.MAD-OUTSTATE | Min OA |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MAD-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MAD-OUTSTATE
|  |  | MSF | Online |  | MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC007
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC010 | ASF.DA-P | 0.001469 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DA-P
|  |  | ASF.RA-T | 69.4183 | deg F | Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RA-T
|  |  | ASF.RA-Q | 443.8686 | ppm | Return Air Quality | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RA-Q | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RA-Q
|  |  | ASF.DA-T | 92.0338 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DA-T
|  |  | ASF.ZN-T | 70.7348 | deg F | Zone Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZN-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZN-T
|  |  | ASF.ASF-O | 40 | % | Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-O
|  |  | ASF.ARF-O | 40 | % | Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-O
|  |  | ASF.CVA-O | 0.1055 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CVA-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CVA-O
|  |  | ASF.WC-ADJ | 0 | deg F | Warmer/Cooler Adjust | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.WC-ADJ | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.WC-ADJ
|  |  | ASF.OA-T | 54.7565 | deg F | Outdoor Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OA-T
|  |  | ASF.HTGOATLOCKOUT-SP | 60 | deg F | Heating OA Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.HTGOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.HTGOATLOCKOUT-SP
|  |  | ASF.OCC-MINCFM | 2000 | cfm | OA Damper Add for ASF Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCC-MINCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCC-MINCFM
|  |  | ASF.DAP-SP | 0.4 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DAP-SP
|  |  | ASF.ZNT-SP | 72 | deg F | Zone Temperature Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZNT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZNT-SP
|  |  | ASF.CLG-O | 100 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-O
|  |  | ASF.RAQ-SP | 520 | ppm | Return Air CO2 Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RAQ-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RAQ-SP
|  |  | ASF.MOAD-O | 2000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MOAD-O
|  |  | ASF.OCC-MAXCFM | 0 | cfm | OA Damper Add for ASF Max CO2 | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCC-MAXCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCC-MAXCFM
|  |  | ASF.OFFDELAY | 30 | seconds | Off Delay | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OFFDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OFFDELAY
|  |  | ASF.ONDELAY | 30 | seconds | On Delay | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ONDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ONDELAY
|  |  | ASF.Stageup Interval | 10 | minutes | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Stageup Interval | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Stageup Interval
|  |  | ASF.Fan Stage 4 Speed | 73 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Stage 4 Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Stage 4 Speed
|  |  | ASF.Fan Stage 3 Speed | 63 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Stage 3 Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Stage 3 Speed
|  |  | ASF.Fan Stage 1 Speed (Min)40 | 40 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Stage 1 Speed (Min)40 | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Stage 1 Speed (Min)
|  |  | ASF.Fan Stage 2 Speed(48.3) | 50 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Stage 2 Speed(48.3) | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Stage 2 Speed
|  |  | ASF.Setpoint Differential | 50 | ppm | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Setpoint Differential | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Setpoint Differential
|  |  | ASF.Stagedown Interval | 10 | minutes | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Stagedown Interval | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Stagedown Interval
|  |  | ASF.OCCMODE-BYPASSTIME | 3600 | seconds | Bypass Time | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCCMODE-BYPASSTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCCMODE-BYPASSTIME
|  |  | ASF.UNOCC-DIFF | 2 | deg F | Differential | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNOCC-DIFF | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNOCC-DIFF
|  |  | ASF.UNOCC-SATTIME | 180 | seconds | Satisfied Timer Duration | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNOCC-SATTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNOCC-SATTIME
|  |  | ASF.PFRESTART-TIME | 60 | seconds | Power Fail Restart Time | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.PFRESTART-TIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.PFRESTART-TIME
|  |  | ASF.EFF DA-P | 0.0013646 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFF DA-P
|  |  | ASF.EFFHTG-SP | 72 | deg F | Effective Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFFHTG-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFFHTG-SP
|  |  | ASF.EFFCLG-SP | 72 | deg F | Effective Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFFCLG-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFFCLG-SP
|  |  | ASF.HTGUNOCC-SP | 65 | deg F | Unocc Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.HTGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.HTGUNOCC-SP
|  |  | ASF.HTGSTBY-SP | 68 | deg F | Standby Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.HTGSTBY-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.HTGSTBY-SP
|  |  | ASF.HTGOCC-SP | 70 | deg F | Occ Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.HTGOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.HTGOCC-SP
|  |  | ASF.CLGUNOCC-SP | 82 | deg F | Unocc Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLGUNOCC-SP
|  |  | ASF.CLGSTBY-SP | 77 | deg F | Standby Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLGSTBY-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLGSTBY-SP
|  |  | ASF.CLGOCC-SP | 70 | deg F | Occ Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLGOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLGOCC-SP
|  |  | ASF.RFMAX-SP | 100 | % | Return Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RFMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RFMAX-SP
|  |  | ASF.RFMIN-SP | 0 | % | Return Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RFMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RFMIN-SP
|  |  | ASF.SFHI-RST | 100 | % | Supply Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SFHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SFHI-RST
|  |  | ASF.SFLO-RST | 0 | % | Supply Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SFLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SFLO-RST
|  |  | ASF.EMERGENCY DAP-SP | 1.5 | in wc | Emergency Duct Static Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EMERGENCY DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EMERGENCY DAP-SP
|  |  | ASF.EMERGENCY SF-O | 70 | % | Emergency On Percent Cmd | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EMERGENCY SF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EMERGENCY SF-O
|  |  | ASF.Ramp Rate | 50 | Change per Minute | Ramp Rate | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Ramp Rate | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Ramp Rate
|  |  | ASF.Fan Run Speed | 40 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.Fan Run Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.Fan Run Speed
|  |  | ASF.OALT-SP | 41 | deg F | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OALT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OALT-SP
|  |  | ASF.EFFDAT-SP | 90 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFFDAT-SP
|  |  | ASF.DATCLGUNOCC-SP | 55 | deg F | Unocc Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATCLGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATCLGUNOCC-SP
|  |  | ASF.DATHTGUNOCC-SP | 90 | deg F | Unocc Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATHTGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATHTGUNOCC-SP
|  |  | ASF.MAD-RAMPRATE | 50 | Change per Minute | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MAD-RAMPRATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MAD-RAMPRATE
|  |  | ASF.RACO2HI-RST | 1000 | ppm | CO2 Reset B | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RACO2HI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RACO2HI-RST
|  |  | ASF.MAD-MINPOS | 2000 | % | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MAD-MINPOS | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MAD-MINPOS
|  |  | ASF.DATCLGMIN-SP | 55 | deg F | Discharge Air Setpoint Cooling Min | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATCLGMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATCLGMIN-SP
|  |  | ASF.DATSATISFIED-SP | 70 | deg F | Discharge Air Setpoint Zone Satisfied | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATSATISFIED-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATSATISFIED-SP
|  |  | ASF.DATHTGMAX-SP | 90 | deg F | Discharge Air Setpoint Heating Max | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATHTGMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATHTGMAX-SP
|  |  | ASF.ASF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-S
|  |  | ASF.ARF-S | On |  | Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-S
|  |  | ASF.LT-A | Normal |  | Low Temperature Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.LT-A | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.LT-A
|  |  | ASF.ASF-C | On |  | Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-C
|  |  | ASF.ARF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-C
|  |  | ASF.RFISO-C | Open |  | Return Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RFISO-C
|  |  | ASF.SFISO-C | Open |  | Supply Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SFISO-C
|  |  | ASF.ZN-TOCC | Inactive |  | Zone Temporary Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZN-TOCC | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZN-TOCC
|  |  | ASF.CLG-EN | TRUE |  | Cooling is Available | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-EN
|  |  | ASF.TUNING-RESET | FALSE |  | Reset PID Tuning | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.TUNING-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.TUNING-RESET
|  |  | ASF.CLG-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-AVAILABLE
|  |  | ASF.RH-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RH-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RH-AVAILABLE
|  |  | ASF.PFRESTART-EN | TRUE |  | Power Fail Restart Enable | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.PFRESTART-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.PFRESTART-EN
|  |  | ASF.RF-Enabled | TRUE |  | Device Enable | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RF-Enabled | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RF-Enabled
|  |  | ASF.OCC-MODE | Occupied |  | Occupancy Status Display | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCC-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCC-MODE
|  |  | ASF.WC-C | Normal |  | Warmup/Cooldown Mode | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.WC-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.WC-C
|  |  | ASF.UNITEN-MODE | Enable |  | Unit Enable Mode | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNITEN-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNITEN-MODE
|  |  | ASF.SYS-RESET | Off |  | System Alarm Reset | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SYS-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SYS-RESET
|  |  | ASF.OCC-SCHEDULE | Occupied |  | Occupancy from Schedule | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.OCC-SCHEDULE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.OCC-SCHEDULE
|  |  | ASF.APP-MODE | Auto |  | Application Mode | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.APP-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.APP-MODE
|  |  | ASF.DELAYTYPE | Off |  | Delay Type | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DELAYTYPE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DELAYTYPE
|  |  | ASF.AHU-STATE | HX Cool+Mech |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.AHU-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.AHU-STATE
|  |  | ASF.ZNT-STATE | Heating |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZNT-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZNT-STATE
|  |  | ASF.EFF-OCC | Occupied |  | Effective Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFF-OCC | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFF-OCC
|  |  | ASF.UNOCC-STATE | Unocc Cntrl Not Req'd |  | Unocc Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNOCC-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNOCC-STATE
|  |  | ASF.UNITEN-STATE | Enable |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.UNITEN-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.UNITEN-STATE
|  |  | ASF.STARTSTOP-STATE | On |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.STARTSTOP-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.STARTSTOP-STATE
|  |  | ASF.NOFLOW-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.NOFLOW-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.NOFLOW-STATE
|  |  | ASF.SMOKE SEQUENCE-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SMOKE SEQUENCE-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SMOKE SEQUENCE-STATE
|  |  | ASF.RF-OUTSTATE | Fan Track Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RF-OUTSTATE
|  |  | ASF.SF-OUTSTATE | Ramp |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.SF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.SF-OUTSTATE
|  |  | ASF.RF-IA | Normal |  | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RF-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RF-IA
|  |  | ASF.RF-Status | On |  | Device Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RF-Status | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RF-Status
|  |  | ASF.RH-OUTSTATE | Off |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RH-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RH-OUTSTATE
|  |  | ASF.CLG-OUTSTATE | T Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-OUTSTATE
|  |  | ASF.MAD-OUTSTATE | Min OA |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MAD-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MAD-OUTSTATE
|  |  | ASF.DATSP-STATE | Heating DA-T Reset |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DATSP-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DATSP-STATE
|  |  | ASF | Online |  | ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC010
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC013 | LSF.DA-P | 0.07192 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DA-P
|  |  | LSF.MA-T | 55.9926 | deg F | Mixed Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MA-T
|  |  | LSF.DA-T | 73.0527 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DA-T
|  |  | LSF.OA-F2 | 6939.207 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-F2 | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-F2
|  |  | LSF.OA-F1 | 7046.188 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-F1 | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-F1
|  |  | LSF.LRA-T | 71.1619 | deg F | Library Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRA-T
|  |  | LSF.OA-T | 54.3803 | deg F | Outdoor Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-T
|  |  | LSF.LSF-O | 50 | % | Library Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-O
|  |  | LSF.CVL-O | 37.4286 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CVL-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CVL-O
|  |  | LSF.LRF-O | 62 | % | Library Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-O
|  |  | LSF.HTGOATLOCKOUT-SP | 60 | deg F | Heating OA Lockout Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.HTGOATLOCKOUT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.HTGOATLOCKOUT-SP
|  |  | LSF.OCC-MINCFM | 2000 | cfm | OA Damper Add for LSF Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OCC-MINCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OCC-MINCFM
|  |  | LSF.DAP-SP | 0.2 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DAP-SP
|  |  | LSF.CLG-O | 0 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-O
|  |  | LSF.MOAD-O | 2000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MOAD-O
|  |  | LSF.OCCSPD-SP | 50 | % | Occupied Supply Fan Speed Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OCCSPD-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OCCSPD-SP
|  |  | LSF.UNOCSPD-SP | 30 | % | Unoccupied Supply Fan Speed Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOCSPD-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOCSPD-SP
|  |  | LSF.UNOC-MINCFM | 2000 | cfm | OA Damper Add for LSF Unoccupied | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOC-MINCFM | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOC-MINCFM
|  |  | LSF.DATHTGMAX-SP | 90 |  | Output Range High | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DATHTGMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DATHTGMAX-SP
|  |  | LSF.DATCLGMIN-SP | 55 |  | Output Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DATCLGMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DATCLGMIN-SP
|  |  | LSF.OATLO-RST | 30 |  | Input Range High | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OATLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OATLO-RST
|  |  | LSF.OATHI-RST | 80 |  | Input Range Low | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OATHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OATHI-RST
|  |  | LSF.OFFDELAY | 30 | seconds | Off Delay | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OFFDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OFFDELAY
|  |  | LSF.ONDELAY | 30 | seconds | On Delay | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.ONDELAY | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.ONDELAY
|  |  | LSF.OCCMODE-BYPASSTIME | 3600 | seconds | Bypass Time | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OCCMODE-BYPASSTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OCCMODE-BYPASSTIME
|  |  | LSF.UNOCC-DIFF | 2 | deg F | Differential | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOCC-DIFF | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOCC-DIFF
|  |  | LSF.UNOCC-SATTIME | 180 | seconds | Satisfied Timer Duration | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOCC-SATTIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOCC-SATTIME
|  |  | LSF.PFRESTART-TIME | 60 | seconds | Power Fail Restart Time | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.PFRESTART-TIME | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.PFRESTART-TIME
|  |  | LSF.EFF DA-P | 0.072259 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EFF DA-P
|  |  | LSF.RFMAX-SP | 124 | % | Return Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RFMAX-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RFMAX-SP
|  |  | LSF.RFMIN-SP | 0 | % | Return Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RFMIN-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RFMIN-SP
|  |  | LSF.SFHI-RST | 100 | % | Supply Fan High | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SFHI-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SFHI-RST
|  |  | LSF.SFLO-RST | 0 | % | Supply Fan Low | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SFLO-RST | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SFLO-RST
|  |  | LSF.EMERGENCY DAP-SP | 1.5 | in wc | Emergency Duct Static Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EMERGENCY DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EMERGENCY DAP-SP
|  |  | LSF.EMERGENCY SF-O | 70 | % | Emergency On Percent Cmd | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EMERGENCY SF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EMERGENCY SF-O
|  |  | LSF.Ramp Rate | 50 | Change per Minute | Ramp Rate | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.Ramp Rate | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.Ramp Rate
|  |  | LSF.Fan Run Speed | 50 | % | Input (Float) | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.Fan Run Speed | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.Fan Run Speed
|  |  | LSF.OALT-SP | 41 | deg F | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OALT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OALT-SP
|  |  | LSF.EFFDAT-SP | 73.0077 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EFFDAT-SP
|  |  | LSF.DATCLGUNOCC-SP | 55 | deg F | Unocc Cooling Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DATCLGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DATCLGUNOCC-SP
|  |  | LSF.DATHTGUNOCC-SP | 90 | deg F | Unocc Heating Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DATHTGUNOCC-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DATHTGUNOCC-SP
|  |  | LSF.MAD-RAMPRATE | 50 | Change per Minute | Present Value | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MAD-RAMPRATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MAD-RAMPRATE
|  |  | LSF.LSF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-S
|  |  | LSF.LT-A | Normal |  | Low Temperature Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LT-A | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LT-A
|  |  | LSF.LRF-S | On |  | Library Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-S
|  |  | LSF.TEF-S | On |  | Toilet Exhaust Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.TEF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.TEF-S
|  |  | LSF.LSF-C | On |  | Library Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-C
|  |  | LSF.LRFISO-C | Open |  | Library Return Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRFISO-C
|  |  | LSF.TEF-C | On |  | Toilet Exhaust Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.TEF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.TEF-C
|  |  | LSF.LRF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-C
|  |  | LSF.SFISO-C | Open |  | Supply Isolation Damper Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SFISO-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SFISO-C
|  |  | LSF.CLG-EN | TRUE |  | Cooling is Available | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-EN
|  |  | LSF.TUNING-RESET | FALSE |  | Reset PID Tuning | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.TUNING-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.TUNING-RESET
|  |  | LSF.CLG-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-AVAILABLE
|  |  | LSF.RH-AVAILABLE | TRUE |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RH-AVAILABLE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RH-AVAILABLE
|  |  | LSF.PFRESTART-EN | TRUE |  | Power Fail Restart Enable | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.PFRESTART-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.PFRESTART-EN
|  |  | LSF.RF-Enabled | TRUE |  | Device Enable | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RF-Enabled | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RF-Enabled
|  |  | LSF.WC-C | Normal |  | Warmup/Cooldown Mode | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.WC-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.WC-C
|  |  | LSF.UNITEN-MODE | Enable |  | Unit Enable Mode | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNITEN-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNITEN-MODE
|  |  | LSF.SYS-RESET | Reset |  | System Alarm Reset | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SYS-RESET | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SYS-RESET
|  |  | LSF.OCC-SCHEDULE | Occupied |  | Occupancy from Schedule | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OCC-SCHEDULE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OCC-SCHEDULE
|  |  | LSF.APP-MODE | Auto |  | Application Mode | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.APP-MODE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.APP-MODE
|  |  | LSF.OUTSTATE | Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OUTSTATE
|  |  | LSF.DELAYTYPE | Off |  | Delay Type | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DELAYTYPE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DELAYTYPE
|  |  | LSF.AHU-STATE | HX Heat+Preheat+Reheat |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.AHU-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.AHU-STATE
|  |  | LSF.EFF-OCC | Occupied |  | Effective Occupancy | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EFF-OCC | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EFF-OCC
|  |  | LSF.UNOCC-STATE | Unocc Cntrl Not Req'd |  | Unocc Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNOCC-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNOCC-STATE
|  |  | LSF.UNITEN-STATE | Enable |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.UNITEN-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.UNITEN-STATE
|  |  | LSF.STARTSTOP-STATE | On |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.STARTSTOP-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.STARTSTOP-STATE
|  |  | LSF.NOFLOW-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.NOFLOW-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.NOFLOW-STATE
|  |  | LSF.SMOKE SEQUENCE-STATE | Normal |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SMOKE SEQUENCE-STATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SMOKE SEQUENCE-STATE
|  |  | LSF.RF-OUTSTATE | Fan Track Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RF-OUTSTATE
|  |  | LSF.SF-OUTSTATE | Ramp |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.SF-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.SF-OUTSTATE
|  |  | LSF.RF-IA | Normal |  | Alarm | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RF-IA | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RF-IA
|  |  | LSF.RF-Status | On |  | Device Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RF-Status | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RF-Status
|  |  | LSF.RH-OUTSTATE | T Control |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.RH-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.RH-OUTSTATE
|  |  | LSF.CLG-OUTSTATE | Off |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-OUTSTATE
|  |  | LSF.MAD-OUTSTATE | Min OA |  | State | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MAD-OUTSTATE | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MAD-OUTSTATE
|  |  | LSF | Online |  | LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC013
MSF-VFD | UW-EMS-OPS>GOWEN HALL>FC-1>MSF-VFD | FAC-JCIDB1:UW-NAE90/FC-1.MSF-VFD | Power [KW] | 1.82 | kW | Actual motor power in KW - P1610 | UW-EMS-OPS>GOWEN HALL>FC-1>MSF-VFD>Power [KW] | FAC-JCIDB1:UW-NAE90/FC-1.MSF-VFD.AV-15

## Sheet3
Controller Information |  |  | Points
Description | Location |  | Name/Label | Value | Units/States | Description | Location
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC005 | HWS.PHWS-T | 140.6453 | deg F | Primary HW Supply Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWS-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWS-T
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC006 | HWS.PHWR-T | 132.2234 | deg F | Primary HW Return Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWR-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWR-T
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC007 | HWS.HX1V2-O | 0.54986 | % | Heat Exchanger 1 Valve 2 Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HX1V2-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HX1V2-O
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC008 | HWS.HX1V1-O | 58.6363 | % | Heat Exchanger 1 Valve 1 Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HX1V1-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HX1V1-O
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC009 | HWS.MAD-O | 99.9982 | % | Mixed Air Damper Output | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MAD-O
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC018 | HWS.HWS-SP | 140.4254 | deg F | Heating Water Temp Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.HWS-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.HWS-SP
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC022 | HWS.OA-FLOW | 14203.738 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.OA-FLOW | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.OA-FLOW
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC023 | HWS.MOAD-REQ | 8000 | cfm | Total Minimum Outdoor Air Required | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.MOAD-REQ | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.MOAD-REQ
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC024 | HWS.CLG-REQ | 99.9981 | % | Maximum Cooling Required | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.CLG-REQ | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.CLG-REQ
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC039 | HWS.PHWP2-S | Off |  | Primary HW Pump 2 Status | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-S
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC040 | HWS.PHWP1-S | On |  | Primary HW Pump 1 Status | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-S
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC041 | HWS.RAD-C | Open |  | Radiant Heating Valve Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.RAD-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.RAD-C
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC042 | HWS.PHWP2-C | Off |  | Primary HW Pump 2 Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP2-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP2-C
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC043 | HWS.PHWP1-C | On |  | Primary HW Pump 1 Command | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.PHWP1-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.PHWP1-C
HWS - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>HWS | FAC-JCIDB1:UW-NAE90/FC-1.FEC044 | HWS.SYSTEM-EN | TRUE |  | Heating System Enable | UW-EMS-OPS>GOWEN HALL>FC-1>HWS>HWS.SYSTEM-EN | FAC-JCIDB1:UW-NAE90/FC-1.FEC004.SYSTEM-EN
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC007 | MSF.DA-P | 0.28066 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DA-P
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC008 | MSF.RA-T | 72.4168 | deg F | Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.RA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.RA-T
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC009 | MSF.DA-T | 73.0233 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DA-T
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC010 | MSF.MSF-O | 60 | % | Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-O
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC011 | MSF.MRF-O | 61.8557 | % | Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-O
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC012 | MSF.CVM-O | 0.39836 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CVM-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CVM-O
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC016 | MSF.DAP-SP | 0.5 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.DAP-SP
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC017 | MSF.CLG-O | 99.9981 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.CLG-O
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC018 | MSF.MOAD-O | 4000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MOAD-O
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC030 | MSF.EFF DA-P | 0.27493 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EFF DA-P
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC040 | MSF.EFFDAT-SP | 72.4727 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.EFFDAT-SP
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC044 | MSF.MSF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-S
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC045 | MSF.MRF-S | On |  | Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-S
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC047 | MSF.MSF-C | On |  | Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MSF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MSF-C
MRF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>MSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC048 | MSF.MRF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>MSF>MSF.MRF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC007.MRF-C
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC010 | ASF.DA-P | 0.001469 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DA-P
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC011 | ASF.RA-T | 69.4183 | deg F | Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RA-T
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC012 | ASF.RA-Q | 443.8686 | ppm | Return Air Quality | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RA-Q | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RA-Q
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC013 | ASF.DA-T | 92.0338 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DA-T
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC014 | ASF.ZN-T | 70.7348 | deg F | Zone Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZN-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZN-T
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC015 | ASF.ASF-O | 40 | % | Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-O
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC016 | ASF.ARF-O | 40 | % | Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-O
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC017 | ASF.CVA-O | 0.1055 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CVA-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CVA-O
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC022 | ASF.DAP-SP | 0.4 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.DAP-SP
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC023 | ASF.ZNT-SP | 72 | deg F | Zone Temperature Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ZNT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ZNT-SP
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC024 | ASF.CLG-O | 100 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.CLG-O
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC025 | ASF.RAQ-SP | 520 | ppm | Return Air CO2 Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.RAQ-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.RAQ-SP
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC026 | ASF.MOAD-O | 2000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.MOAD-O
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC041 | ASF.EFF DA-P | 0.0013646 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFF DA-P
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC059 | ASF.EFFDAT-SP | 90 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.EFFDAT-SP
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC068 | ASF.ASF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-S
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC069 | ASF.ARF-S | On |  | Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-S
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC071 | ASF.ASF-C | On |  | Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ASF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ASF-C
ASF AHU -BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>ASF | FAC-JCIDB1:UW-NAE90/FC-1.FEC072 | ASF.ARF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>ASF>ASF.ARF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC010.ARF-C
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC013 | LSF.DA-P | 0.07192 | in wc | Discharge Air Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DA-P
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC014 | LSF.MA-T | 55.9926 | deg F | Mixed Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MA-T
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC015 | LSF.DA-T | 73.0527 | deg F | Discharge Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DA-T
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC016 | LSF.OA-F2 | 6939.207 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-F2 | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-F2
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC017 | LSF.OA-F1 | 7046.188 | cfm | Outdoor Air Flow | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-F1 | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-F1
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC018 | LSF.LRA-T | 71.1619 | deg F | Library Return Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRA-T
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC019 | LSF.OA-T | 54.3803 | deg F | Outdoor Air Temperature | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.OA-T | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.OA-T
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC020 | LSF.LSF-O | 50 | % | Library Supply Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-O
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC021 | LSF.CVL-O | 37.4286 | % | Reheat Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CVL-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CVL-O
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC022 | LSF.LRF-O | 62 | % | Library Return Fan Output | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-O
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC025 | LSF.DAP-SP | 0.2 | in wc | Discharge Air Pressure Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.DAP-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.DAP-SP
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC026 | LSF.CLG-O | 0 | % | Cooling Request | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.CLG-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.CLG-O
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC027 | LSF.MOAD-O | 2000 | cfm | Minimum Outdoor Air Damper Request | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.MOAD-O | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.MOAD-O
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC041 | LSF.EFF DA-P | 0.072259 | in wc | Duct Static Pressure | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EFF DA-P | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EFF DA-P
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC051 | LSF.EFFDAT-SP | 73.0077 | deg F | Discharge Air Setpoint | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.EFFDAT-SP | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.EFFDAT-SP
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC055 | LSF.LSF-S | On |  | Supply Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-S
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC057 | LSF.LRF-S | On |  | Library Return Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-S
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC058 | LSF.TEF-S | On |  | Toilet Exhaust Fan Status | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.TEF-S | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.TEF-S
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC059 | LSF.LSF-C | On |  | Library Supply Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LSF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LSF-C
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC061 | LSF.TEF-C | On |  | Toilet Exhaust Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.TEF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.TEF-C
LSF AHU - BASEMENT | UW-EMS-OPS>GOWEN HALL>FC-1>LSF | FAC-JCIDB1:UW-NAE90/FC-1.FEC062 | LSF.LRF-C | On |  | Return Fan Command | UW-EMS-OPS>GOWEN HALL>FC-1>LSF>LSF.LRF-C | FAC-JCIDB1:UW-NAE90/FC-1.FEC013.LRF-C
MSF-VFD | UW-EMS-OPS>GOWEN HALL>FC-1>MSF-VFD | FAC-JCIDB1:UW-NAE90/FC-1.MSF-VFD | Power [KW] | 1.82 | kW | Actual motor power in KW - P1610 | UW-EMS-OPS>GOWEN HALL>FC-1>MSF-VFD>Power [KW] | FAC-JCIDB1:UW-NAE90/FC-1.MSF-VFD.AV-15